## 11kV, 415V powerlines & kiosks
[15 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
EGN 423: EMF Calculator | [14 empty] | 3.0452 | 2.8827 | 2.5576 | 2.1693 | 1.7956 | 1.4729 | 1.2092 | 0.99888 | 0.83244 | 0.70054 | 0.59537 | 0.51079 | 0.44211 | 0.3858 | 0.33919 | 0.30027 | 0.26749 | 0.23966 | 0.21586 | 0.19536 | 0.1776 | 0.16211 | 0.14853 | 0.13657 | 0.12597 | 0.11655 | 0.10813 | 0.10059 | 0.093799 | 0.087668 | 0.082114
Version 4.1 - 4 July 2018 | [14 empty] | 0: NOTE: Green results are in uT
11 kV, 415 V power lines and kiosks | [14 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
[14 empty] | 415V (6m clearance) | 3.0452 | 2.8827 | 2.5576 | 2.1693 | 1.7956 | 1.4729 | 1.2092 | 0.99888 | 0.83244 | 0.70054 | 0.59537 | 0.51079 | 0.44211 | 0.3858 | 0.33919 | 0.30027 | 0.26749 | 0.23966 | 0.21586 | 0.19536 | 0.1776 | 0.16211 | 0.14853 | 0.13657 | 0.12597 | 0.11655 | 0.10813 | 0.10059 | 0.093799 | 0.087668 | 0.082114
[9 empty] | Magnetic field |  |  |  |  | 11kV (6.7m clearance) | 5.1321 | 4.9755 | 4.5911 | 4.0673 | 3.5041 | 2.9713 | 2.5031 | 2.1087 | 1.7834 | 1.5175 | 1.3006 | 1.123 | 0.97681 | 0.85571 | 0.75466 | 0.66971 | 0.59778 | 0.53645 | 0.48381 | 0.43834 | 0.39883 | 0.36432 | 0.33401 | 0.30725 | 0.28353 | 0.26241 | 0.24353 | 0.22659 | 0.21133 | 0.19755 | 0.18505
[9 empty] | 1.4729 |  |  |  |  | UG 11kV (depth 1m) | 0.44353 | 0.36498 | 0.22374 | 0.13435 | 0.085756 | 0.058401 | 0.041965 | 0.031467 | 0.024406 | 0.019451 | 0.015849 | 0.013154 | 0.011088 | 0.0094694 | 0.0081792 | 0.0071346 | 0.0062772 | 0.005565 | 0.004967 | 0.0044602 | 0.004027 | 0.0036538 | 0.0033301 | 0.0030475 | 0.0027993 | 0.0025802 | 0.0023858 | 0.0022125 | 0.0020574 | 0.0019181 | 0.0017924
[14 empty] | 415V ABC (6m clearance) | 0.045166 | 0.043781 | 0.039512 | 0.033847 | 0.028131 | 0.023085 | 0.018919 | 0.015585 | 0.012947 | 0.01086 | 0.0092008 | 0.0078702 | 0.0067933 | 0.0059132 | 0.005187 | 0.0045822 | 0.0040742 | 0.003644 | 0.0032769 | 0.0029614 | 0.0026885 | 0.002451 | 0.0022431 | 0.0020602 | 0.0018985 | 0.0017548 | 0.0016267 | 0.001512 | 0.0014089 | 0.0013159 | 0.0012317
[14 empty] | Kiosk | 9.72 | 1.008 | 0.448 | 0.28 | 0.164 | 0.104 | 0.04 | 0.02 | Negligible | Negligible | Negligible | Negligible | Negligible | Negligible | Negligible | Negligible | Negligible | Negligible | Negligible | Negligible | Negligible | Negligible | Negligible | Negligible | Negligible | Negligible | Negligible | Negligible | Negligible | Negligible | Negligible | Neglegible
NOTE: All results below are in mG
[14 empty] | 415V (6m clearance) | 30.4518 | 28.8275 | 25.5759 | 21.6933 | 17.9561 | 14.7295 | 12.0921 | 9.9888 | 8.3244 | 7.0054 | 5.9537 | 5.1079 | 4.4211 | 3.858 | 3.3919 | 3.0027 | 2.6749 | 2.3966 | 2.1586 | 1.9536 | 1.776 | 1.6211 | 1.4853 | 1.3657 | 1.2597 | 1.1655 | 1.0813 | 1.0059 | 0.93799 | 0.87668 | 0.82114
[15 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
| Source |  | 7 |  |  |  | STEP 1 |  | 6 | -0.8 | 100 | 0 | 1 | -2m | 2.9959 | 2.93 | 2.7848 | 2.5825 | 2.3491 | 2.1073 | 1.8735 | 1.6573 | 1.4632 | 1.2922 | 1.1432 | 1.0142 | 0.90282 | 0.80666 | 0.72352 | 0.65148 | 0.58886 | 0.53425 | 0.48643 | 0.44441 | 0.40734 | 0.37451 | 0.34534 | 0.31933 | 0.29604 | 0.27513 | 0.2563 | 0.23928 | 0.22386 | 0.20985 | 0.19709
[9 empty] | 6 | -0.31 | 100 | 120 | 2 | 0m | 5.3063 | 5.1045 | 4.6815 | 4.1385 | 3.5707 | 3.0407 | 2.5766 | 2.1847 | 1.8595 | 1.5918 | 1.3716 | 1.19 | 1.0395 | 0.91404 | 0.80873 | 0.71975 | 0.64408 | 0.57929 | 0.52349 | 0.47513 | 0.433 | 0.3961 | 0.36361 | 0.33488 | 0.30936 | 0.2866 | 0.26622 | 0.24791 | 0.2314 | 0.21646 | 0.2029
| Load used for calculation (use LV Amps for kiosk) | 400 | 3 |  |  | Amps | STEP 2 |  | 6 | 0.31 | 100 | 240 | 3 | 1m | 7.6129 | 7.2069 | 6.394 | 5.4233 | 4.489 | 3.6824 | 3.023 | 2.4972 | 2.0811 | 1.7514 | 1.4884 | 1.277 | 1.1053 | 0.9645 | 0.84797 | 0.75066 | 0.66871 | 0.59914 | 0.53964 | 0.4884 | 0.44399 | 0.40527 | 0.37133 | 0.34142 | 0.31493 | 0.29137 | 0.27034 | 0.25147 | 0.2345 | 0.21917 | 0.20528
[13 empty] | 4 | 2m | 11.8154 | 10.874 | 9.131 | 7.2771 | 5.6896 | 4.453 | 3.5233 | 2.8288 | 2.3062 | 1.908 | 1.6 | 1.3582 | 1.1656 | 1.0101 | 0.88304 | 0.77801 | 0.69032 | 0.61643 | 0.55362 | 0.49982 | 0.45341 | 0.4131 | 0.37789 | 0.34696 | 0.31964 | 0.2954 | 0.2738 | 0.25446 | 0.2371 | 0.22144 | 0.20727
| Perpendicular distance from power line, d | [5 empty] | STEP 3 | [5 empty] | 5 | 4m | 44.8166 | 34.3113 | 21.6149 | 13.4959 | 8.8829 | 6.1888 | 4.5252 | 3.439 | 2.6956 | 2.1667 | 1.7778 | 1.4841 | 1.2571 | 1.0781 | 0.93457 | 0.81773 | 0.72141 | 0.64109 | 0.57343 | 0.51591 | 0.46661 | 0.42403 | 0.38701 | 0.35463 | 0.32614 | 0.30094 | 0.27855 | 0.25857 | 0.24065 | 0.22454 | 0.20999
[13 empty] | 6 | 6m | 1053.5132 | 160.0753 | 41.3718 | 19.0349 | 10.9573 | 7.1207 | 4.9999 | 3.7055 | 2.8563 | 2.269 | 1.8461 | 1.5313 | 1.2908 | 1.1028 | 0.95305 | 0.83185 | 0.73237 | 0.64973 | 0.58033 | 0.52149 | 0.47116 | 0.42779 | 0.39014 | 0.35725 | 0.32836 | 0.30283 | 0.28017 | 0.25996 | 0.24186 | 0.22559 | 0.2109
| Height above ground, h | [5 empty] | STEP 4 | [5 empty] | 7 | 8m | 44.8166 | 34.3113 | 21.6149 | 13.4959 | 8.8829 | 6.1888 | 4.5252 | 3.439 | 2.6956 | 2.1667 | 1.7778 | 1.4841 | 1.2571 | 1.0781 | 0.93457 | 0.81773 | 0.72141 | 0.64109 | 0.57343 | 0.51591 | 0.46661 | 0.42403 | 0.38701 | 0.35463 | 0.32614 | 0.30094 | 0.27855 | 0.25857 | 0.24065 | 0.22454 | 0.20999
| (kiosk results only for 1m) | [11 empty] | 8 | 10m | 11.8154 | 10.874 | 9.131 | 7.2771 | 5.6896 | 4.453 | 3.5233 | 2.8288 | 2.3062 | 1.908 | 1.6 | 1.3582 | 1.1656 | 1.0101 | 0.88304 | 0.77801 | 0.69032 | 0.61643 | 0.55362 | 0.49982 | 0.45341 | 0.4131 | 0.37789 | 0.34696 | 0.31964 | 0.2954 | 0.2738 | 0.25446 | 0.2371 | 0.22144 | 0.20727
| Magnetic field at (d, h) | 1.4729 |  |  |  | uT | Answer
[14 empty] | 11kV (6.7m clearance) | 51.3213 | 49.7552 | 45.9107 | 40.6729 | 35.0413 | 29.7127 | 25.0313 | 21.0868 | 17.8339 | 15.1754 | 13.0057 | 11.2297 | 9.7681 | 8.5571 | 7.5466 | 6.6971 | 5.9778 | 5.3645 | 4.8381 | 4.3834 | 3.9883 | 3.6432 | 3.3401 | 3.0725 | 2.8353 | 2.6241 | 2.4353 | 2.2659 | 2.1133 | 1.9755 | 1.8505
[15 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
If the above answer is above typical background levels (0.1-0.2uT) then consider prudent avoidance (see notes above) | [8 empty] | 6.7 | -1.2 | 100 | 0 | 1 | -2m | 5.6231 | 5.5435 | 5.3367 | 5.0282 | 4.6528 | 4.2448 | 3.8334 | 3.4388 | 3.0733 | 2.7426 | 2.4478 | 2.1878 | 1.9596 | 1.76 | 1.5855 | 1.4329 | 1.2993 | 1.1819 | 1.0785 | 0.98725 | 0.90641 | 0.83456 | 0.7705 | 0.7132 | 0.66179 | 0.61554 | 0.57381 | 0.53604 | 0.50177 | 0.47059 | 0.44215
[9 empty] | 6.7 | 0.6 | 100 | 120 | 2 | 0m | 9.3795 | 9.1644 | 8.623 | 7.8556 | 6.9827 | 6.107 | 5.2924 | 4.5696 | 3.9461 | 3.4168 | 2.9708 | 2.596 | 2.2806 | 2.0145 | 1.789 | 1.597 | 1.4326 | 1.2912 | 1.1687 | 1.0623 | 0.96924 | 0.88752 | 0.81542 | 0.75152 | 0.69466 | 0.64387 | 0.59834 | 0.55739 | 0.52042 | 0.48695 | 0.45656
| Magnetic field reduction considerations (hover over cell for examples) | [7 empty] | 6.7 | 1.2 | 100 | 240 | 3 | 1m | 12.8303 | 12.4388 | 11.4777 | 10.1682 | 8.7603 | 7.4282 | 6.2578 | 5.2717 | 4.4585 | 3.7939 | 3.2514 | 2.8074 | 2.442 | 2.1393 | 1.8866 | 1.6743 | 1.4944 | 1.3411 | 1.2095 | 1.0958 | 0.99708 | 0.91079 | 0.83501 | 0.76814 | 0.70884 | 0.65603 | 0.60882 | 0.56647 | 0.52833 | 0.49387 | 0.46264
| Overhead distribution | [11 empty] | 4 | 2m | 18.5573 | 17.7743 | 15.9163 | 13.5358 | 11.1645 | 9.0918 | 7.3979 | 6.0565 | 5.006 | 4.1823 | 3.532 | 3.0138 | 2.5964 | 2.2567 | 1.9772 | 1.7452 | 1.5506 | 1.3861 | 1.246 | 1.1257 | 1.0217 | 0.93128 | 0.8522 | 0.78265 | 0.72118 | 0.66659 | 0.6179 | 0.57432 | 0.53515 | 0.49982 | 0.46786
| Underground distribution | [11 empty] | 5 | 4m | 50.8863 | 46.3144 | 36.4354 | 26.2728 | 18.6308 | 13.475 | 10.0442 | 7.7112 | 6.0781 | 4.9008 | 4.0287 | 3.367 | 2.8537 | 2.4481 | 2.1225 | 1.8571 | 1.6383 | 1.4557 | 1.3019 | 1.1711 | 1.0589 | 0.9621 | 0.87791 | 0.80428 | 0.7395 | 0.68221 | 0.63131 | 0.58587 | 0.54517 | 0.50855 | 0.47549
| Distribution substations | [11 empty] | 6 | 6m | 273.5114 | 283.5359 | 120.6758 | 50.8244 | 27.7364 | 17.5006 | 12.0665 | 8.8344 | 6.7492 | 5.3246 | 4.3088 | 3.5593 | 2.9902 | 2.5476 | 2.1967 | 1.9136 | 1.682 | 1.4901 | 1.3293 | 1.1932 | 1.077 | 0.97695 | 0.89026 | 0.81462 | 0.74823 | 0.68964 | 0.63766 | 0.59134 | 0.5499 | 0.51266 | 0.47908
[13 empty] | 7 | 8m | 151.598 | 133.4677 | 80.4832 | 43.0732 | 25.4582 | 16.6045 | 11.6486 | 8.6123 | 6.6197 | 5.2444 | 4.2565 | 3.5237 | 2.9651 | 2.5295 | 2.1832 | 1.9034 | 1.6741 | 1.4839 | 1.3244 | 1.1892 | 1.0737 | 0.9743 | 0.88805 | 0.81278 | 0.74668 | 0.68832 | 0.63653 | 0.59037 | 0.54906 | 0.51193 | 0.47845
Results shown for a loading of |  | General comparison of construction types with same load | [5 empty] | 0.001 |  |  |  |  | 8 | 10m | 35.7457 | 33.2016 | 27.5653 | 21.2867 | 15.9858 | 12.0471 | 9.234 | 7.2277 | 5.7757 | 4.7034 | 3.8952 | 3.2735 | 2.7865 | 2.3986 | 2.0852 | 1.8286 | 1.6161 | 1.4382 | 1.2878 | 1.1597 | 1.0496 | 0.95441 | 0.87151 | 0.7989 | 0.73496 | 0.67835 | 0.62799 | 0.58302 | 0.54269 | 0.5064 | 0.47361
400 | Amps |  |  | Amps |  |  |  | 0.25
[8 empty] | 0.5 | [5 empty] | UG 11kV (depth 1m) | 4.4353 | 3.6498 | 2.2374 | 1.3435 | 0.85756 | 0.58401 | 0.41965 | 0.31467 | 0.24406 | 0.19451 | 0.15849 | 0.13154 | 0.11088 | 0.094694 | 0.081792 | 0.071346 | 0.062772 | 0.05565 | 0.04967 | 0.044602 | 0.04027 | 0.036538 | 0.033301 | 0.030475 | 0.027993 | 0.025802 | 0.023858 | 0.022125 | 0.020574 | 0.019181 | 0.017924
Distance | uT | [6 empty] | 1 | [6 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
0m | 3.0452 | [6 empty] | 2 | -0.902 | 0.1 | 100 | 0 | 1 | -2m | 3.2908 | 2.0081 | 0.84048 | 0.42029 | 0.24591 | 0.15997 | 0.11194 | 0.082551 | 0.063325 | 0.050083 | 0.040585 | 0.033546 | 0.028187 | 0.024013 | 0.020701 | 0.018029 | 0.015842 | 0.014029 | 0.012511 | 0.011225 | 0.010129 | 0.0091848 | 0.0083669 | 0.0076536 | 0.0070276 | 0.0064754 | 0.0059858 | 0.0055497 | 0.0051595 | 0.0048091 | 0.0044931
1m | 2.8827 | [6 empty] | 3 | -0.9 | 0.1 | 100 | 120 | 2 | 0m | 4.8823 | 2.5068 | 0.91682 | 0.43855 | 0.25205 | 0.16254 | 0.11319 | 0.083231 | 0.063725 | 0.050333 | 0.040749 | 0.033658 | 0.028265 | 0.024071 | 0.020744 | 0.018061 | 0.015867 | 0.014049 | 0.012526 | 0.011238 | 0.010139 | 0.0091931 | 0.0083738 | 0.0076594 | 0.0070325 | 0.0064796 | 0.0059894 | 0.0055527 | 0.0051621 | 0.0048113 | 0.0044951
2m | 2.5576 |  | 1.7956 | 1.4729 | 1.2092 |  |  | 4 | -0.9 | 0.12 | 100 | 240 | 3 | 1m | 1.1088 | 0.91244 | 0.55936 | 0.33588 | 0.21439 | 0.146 | 0.10491 | 0.078667 | 0.061015 | 0.048627 | 0.039624 | 0.032886 | 0.027719 | 0.023674 | 0.020448 | 0.017837 | 0.015693 | 0.013912 | 0.012418 | 0.011151 | 0.010068 | 0.0091346 | 0.0083252 | 0.0076187 | 0.0069982 | 0.0064504 | 0.0059645 | 0.0055313 | 0.0051436 | 0.0047953 | 0.0044811
3m | 2.1693 | [6 empty] | 5 |  |  |  |  | 4 | 2m | 0.47696 | 0.43655 | 0.33529 | 0.23969 | 0.17067 | 0.12432 | 0.093228 | 0.071909 | 0.05687 | 0.045957 | 0.037833 | 0.031643 | 0.026831 | 0.023022 | 0.019961 | 0.017464 | 0.015404 | 0.013685 | 0.012236 | 0.011004 | 0.0099479 | 0.009036 | 0.0082433 | 0.00755 | 0.0069402 | 0.0064011 | 0.0059223 | 0.005495 | 0.0051122 | 0.0047679 | 0.0044572
4m | 1.7956 | [11 empty] | 5 | 4m | 0.16725 | 0.16199 | 0.14566 | 0.12415 | 0.10265 | 0.083848 | 0.068452 | 0.056215 | 0.046584 | 0.038999 | 0.032988 | 0.028181 | 0.0243 | 0.021134 | 0.018525 | 0.016356 | 0.014535 | 0.012995 | 0.011681 | 0.010553 | 0.009578 | 0.0087298 | 0.0079877 | 0.007335 | 0.0067581 | 0.0062459 | 0.0057892 | 0.0053802 | 0.0050127 | 0.0046813 | 0.0043814
5m | 1.4729 | [11 empty] | 6 | 6m | 0.084369 | 0.08301 | 0.078502 | 0.071799 | 0.064041 | 0.056181 | 0.048823 | 0.042262 | 0.036577 | 0.031731 | 0.027634 | 0.024179 | 0.021265 | 0.0188 | 0.016707 | 0.014922 | 0.013392 | 0.012073 | 0.010931 | 0.0099374 | 0.009068 | 0.0083041 | 0.0076298 | 0.0070321 | 0.0065002 | 0.0060249 | 0.0055988 | 0.0052155 | 0.0048694 | 0.0045561 | 0.0042715
6m | 1.2092 | [11 empty] | 7 | 8m | 0.050717 | 0.050223 | 0.048537 | 0.045888 | 0.042591 | 0.038966 | 0.035278 | 0.03172 | 0.028406 | 0.025395 | 0.022701 | 0.020316 | 0.018219 | 0.016379 | 0.014767 | 0.013355 | 0.012116 | 0.011027 | 0.010066 | 0.0092172 | 0.0084645 | 0.0077951 | 0.007198 | 0.0066636 | 0.0061841 | 0.0057524 | 0.0053628 | 0.00501 | 0.0046898 | 0.0043985 | 0.0041327
7m | 0.99888 | [11 empty] | 8 | 10m | 0.033815 | 0.033595 | 0.032832 | 0.031599 | 0.03 | 0.028154 | 0.026178 | 0.024166 | 0.022194 | 0.020312 | 0.018551 | 0.016927 | 0.015446 | 0.014103 | 0.012891 | 0.011802 | 0.010824 | 0.0099459 | 0.0091578 | 0.0084497 | 0.0078128 | 0.0072391 | 0.0067213 | 0.0062531 | 0.0058289 | 0.0054439 | 0.0050936 | 0.0047743 | 0.0044827 | 0.0042158 | 0.003971
8m | 0.83244
9m | 0.70054 | [12 empty] | 415V ABC (6m clearance) | 0.45166 | 0.43781 | 0.39512 | 0.33847 | 0.28131 | 0.23085 | 0.18919 | 0.15585 | 0.12947 | 0.1086 | 0.092008 | 0.078702 | 0.067933 | 0.059132 | 0.05187 | 0.045822 | 0.040742 | 0.03644 | 0.032769 | 0.029614 | 0.026885 | 0.02451 | 0.022431 | 0.020602 | 0.018985 | 0.017548 | 0.016267 | 0.01512 | 0.014089 | 0.013159 | 0.012317
10m | 0.59537 |  | 0.44211 | 0.3858 | 0.33919 | [9 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
11m | 0.51079 | [7 empty] | 6.01 | 0.1 | 100 | 0 | 1 | -2m | 0.044143 | 0.043604 | 0.041805 | 0.03904 | 0.035694 | 0.032129 | 0.02862 | 0.025341 | 0.022375 | 0.019752 | 0.017461 | 0.015475 | 0.013759 | 0.012279 | 0.010999 | 0.009892 | 0.0089305 | 0.0080927 | 0.0073602 | 0.0067172 | 0.0061507 | 0.0056497 | 0.0052049 | 0.0048087 | 0.0044544 | 0.0041366 | 0.0038507 | 0.0035926 | 0.0033589 | 0.0031467 | 0.0029536
12m | 0.44211 | [7 empty] | 6 | 0.1 | 100 | 120 | 2 | 0m | 0.078443 | 0.076757 | 0.07135 | 0.063655 | 0.055215 | 0.047127 | 0.039944 | 0.033833 | 0.028747 | 0.024556 | 0.021112 | 0.018276 | 0.01593 | 0.013979 | 0.012344 | 0.010967 | 0.0097972 | 0.008798 | 0.007939 | 0.0071961 | 0.0065498 | 0.0059846 | 0.0054879 | 0.0050492 | 0.0046601 | 0.0043134 | 0.0040034 | 0.0037252 | 0.0034745 | 0.003248 | 0.0030427
13m | 0.3858 | [7 empty] | 6 | 0.11 | 100 | 240 | 3 | 1m | 0.11292 | 0.10945 | 0.09878 | 0.084618 | 0.070327 | 0.057711 | 0.047297 | 0.038963 | 0.032368 | 0.027151 | 0.023002 | 0.019676 | 0.016983 | 0.014783 | 0.012967 | 0.011456 | 0.010186 | 0.00911 | 0.0081922 | 0.0074035 | 0.0067212 | 0.0061274 | 0.0056077 | 0.0051504 | 0.0047462 | 0.0043871 | 0.0040668 | 0.00378 | 0.0035222 | 0.0032896 | 0.0030792
14m | 0.33919 | [11 empty] | 4 | 2m | 0.17632 | 0.16802 | 0.14412 | 0.11583 | 0.090625 | 0.070707 | 0.055685 | 0.044483 | 0.036088 | 0.029721 | 0.02482 | 0.020991 | 0.017954 | 0.015513 | 0.013526 | 0.011889 | 0.010527 | 0.0093823 | 0.0084117 | 0.0075823 | 0.0068682 | 0.0062494 | 0.0057097 | 0.0052364 | 0.004819 | 0.0044493 | 0.0041202 | 0.0038261 | 0.0035622 | 0.0033245 | 0.0031097
15m | 0.30027 | [11 empty] | 5 | 4m | 0.70256 | 0.587 | 0.37163 | 0.22804 | 0.14735 | 0.10106 | 0.072938 | 0.054847 | 0.042622 | 0.034016 | 0.027746 | 0.023046 | 0.019437 | 0.016608 | 0.014351 | 0.012522 | 0.01102 | 0.0097719 | 0.0087235 | 0.0078347 | 0.0070748 | 0.0064199 | 0.0058517 | 0.0053556 | 0.0049198 | 0.0045351 | 0.0041937 | 0.0038894 | 0.003617 | 0.0033722 | 0.0031514
16m | 0.26749 | [11 empty] | 6 | 6m | 131.3049 | 3.4744 | 0.78425 | 0.33677 | 0.18619 | 0.11794 | 0.081338 | 0.059465 | 0.04536 | 0.035737 | 0.028881 | 0.023824 | 0.019987 | 0.017008 | 0.014649 | 0.012748 | 0.011195 | 0.0099091 | 0.0088328 | 0.0079228 | 0.0071465 | 0.0064789 | 0.0059007 | 0.0053966 | 0.0049544 | 0.0045645 | 0.0042188 | 0.003911 | 0.0036356 | 0.0033884 | 0.0031655
17m | 0.23966 | [11 empty] | 7 | 8m | 0.70795 | 0.59076 | 0.37314 | 0.22861 | 0.14759 | 0.10118 | 0.072998 | 0.054882 | 0.042644 | 0.03403 | 0.027756 | 0.023053 | 0.019442 | 0.016612 | 0.014354 | 0.012524 | 0.011022 | 0.0097733 | 0.0087247 | 0.0078357 | 0.0070756 | 0.0064206 | 0.0058523 | 0.0053561 | 0.0049203 | 0.0045355 | 0.0041941 | 0.0038897 | 0.0036173 | 0.0033724 | 0.0031516
18m | 0.21586 | [11 empty] | 8 | 10m | 0.17701 | 0.16865 | 0.14458 | 0.11613 | 0.09081 | 0.070821 | 0.055756 | 0.044529 | 0.036119 | 0.029742 | 0.024836 | 0.021002 | 0.017963 | 0.01552 | 0.013531 | 0.011893 | 0.01053 | 0.009385 | 0.0084139 | 0.0075842 | 0.0068698 | 0.0062507 | 0.0057109 | 0.0052374 | 0.00482 | 0.0044501 | 0.0041209 | 0.0038267 | 0.0035627 | 0.003325 | 0.0031102
19m | 0.19536
20m | 0.1776
[14 empty] | Kiosk | 97.2 | 10.08 | 4.48 | 2.8 | 1.64 | 1.04 | 0.4 | 0.2 | Negligible | Negligible | Negligible | Negligible | Negligible | Negligible | Negligible | Negligible | Negligible | Negligible | Negligible | Negligible | Negligible | Negligible | Negligible | Negligible | Negligible | Negligible | Negligible | Negligible | Negligible | Negligible | Negligible | Neglegible
[11 empty] | 100A, mG |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
[10 empty] | 0m | 24.3 |  | 1 | -2m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 1m | 2.52 |  | 2 | 0m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 2m | 1.12 |  | 3 | 1m | 24.3 | 2.52 | 1.12 | 0.7 | 0.41 | 0.26 | 0.1 | 0.05 | Not calculated | Not calculated | Not calculated | Not calculated | Not calculated | Not calculated | Not calculated | Not calculated | Not calculated | Not calculated | Not calculated | Not calculated | Not calculated | Not calculated | Not calculated | Not calculated | Not calculated | Not calculated | Not calculated | Not calculated | Not calculated | Not calculated | Not calculated
[10 empty] | 3m | 0.7 |  | 4 | 2m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 4m | 0.41 |  | 5 | 4m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 5m | 0.26 |  | 6 | 6m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 6m | 0.1 |  | 7 | 8m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 7m | 0.05 |  | 8 | 10m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[14 empty] | height | 0: dist; 1: construction type
[14 empty] | 3 | 0: 6; 1: 1
[14 empty] | -2m | 0: 0m; 1: 415V (6m clearance)
[14 empty] | 0m | 0: 1m; 1: 11kV (6.7m clearance)
[14 empty] | 1m | 0: 2m; 1: UG 11kV (depth 1m)
[14 empty] | 2m | 0: 3m; 1: 415V ABC (6m clearance)
[14 empty] | 4m | 0: 4m; 1: Kiosk
6m | bar: 0
8m | bar: 0
10m | bar: 0
8m
9m
10m
11m
12m
13m
14m
15m
16m
17m
18m
19m
20m
21m
22m
23m
24m
25m
26m
27m
28m
29m
30m
Note on B29: •Minimise loads by optimising network configuration. •Bundle conductors. •Twist conductors (eg. ABC). •Minimise stray currents and residual currents. •Balance loads across all phases to reduce neutral currents. •Avoid phase-by-phase grouping of conductors in parallel circuits. •Install circuits on sides of the road which are less populated. •Consider alternate routes. •Increase the balancing of loads between dual circuit feeders.
Note on B30: •Minimise loads by optimising network configuration. •Use multicore or trefoil cables in preference to three single phase cables. •Place neutral conductors with the associated phase conductors. •Minimise stray currents and residual currents. •Balance loads across all phases to reduce neutral currents. •Avoid phase-by-phase grouping of single core cables in parallel circuits.
Note on B31: •Minimise loads by optimising network configuration. •Consider alternate sites for substation (taking into account incoming and outgoing feeders). •Site substation close to load centre. •Plan the substation layout with its LV side further away from the location of interest than its HV side. •Orientate equipment with uneven field patterns so that the highest field side is turned away from the location of interest (the LV side usually has the highest fields). •Avoid direct ceiling/floor mounting of heavy current cables, open type busbars or disconnector switches, depending on adjoining uses. •Locate cable trays away from walls/ceilings/floors depending on adjoining uses. •Use compact arrangement of underground cables/busbars and secondary connections. •Design busbars to minimise separation between phases and the neutral bus. •Use multicore or trefoil cables in preference to three single phase cables. •Place neutral conductors with the associated phase conductors. •Minimise stray currents and residual currents. •Balance loads across all phases to reduce neutral currents. •Avoid phase-by-phase grouping of single core cables in parallel circuits.
NOTE ON GUIDELINES
- ARPANSA currently recommends compliance with the ICNIRP 2010 guidelines and these have a public exposure level of 200uT.
NOTES ON PRUDENT AVOIDANCE
- Ausgrid's policy includes "taking reasonable steps to limit field exposures from new facilities by locating and operating our electrical installations prudently within current health guidelines as established by Australian health authorities"
- Measures to reduce EMF should be used if they are effective, can be implemented at low cost and do not compromise other factors.
- Prudent avoidance does not operate in isolation, but rather is one of many issues that need to be given due consideration.
- There is no scientific basis for the adoption of arbitrary low exposure limits or setbacks.
- Where field levels are consistent with typical background levels (0.1-0.2uTG) then the potential for further reductions is limited.
- Undergrounding for reasons of EMF alone is clearly outside the scope of prudent avoidance due to the additional cost.
- The results below are indicative only and in most cases will be sufficient to demonstrate the application of prudent avoidance.
- Prudent avoidance is about considering ways to reduce exposure, not accurately predicting the fields at any particular point.
INSTRUCTIONS
Use the EMF calculator to predict the magnetic field from the installation at the nearest receiver.
STEP 1: Indicate the type of installation.
STEP 2: Indicate the load (current) in Amps that the installation will be carrying. Use the calculation in the 'VA to Amp calcs' worksheet to determine the Amps based on the voltage and VA.
STEP 3: Using the diagram as a guide, determine the perpendicular distance (d) from the installation to the nearest receiver.
STEP 4: Determine the height (h) of the nearest receiver above the ground. Not relevant for kiosks.

## Multicore cables
EGN 423: EMF Calculator
Version 4 - 10 March 2016
Multicore cables | [6 empty] | Multicore cables
| Method 1 |  |  |  | Method 2 |  |  |  | Pitch calculator
| Point Calculation |  |  |  | Point Calculation
| Most accurate, however |  |  |  | Error <10% if P>10xa & r>P |  |  |  | Length of circuit | 1000 | m
| Only applicable for typical cable types | [7 empty] | Pitch (P) | 2 | m
| Radius (a) | 0.011547 | m |  | Radius (a) | 0.011547 | m |  | Spacing between conductors | 0.02 | m
| Pitch (P) | 2 | m |  | Pitch (P) | 2 | m |  | Number of turns | 500
| Current (l) | 400 | A |  | Current (I) | 250 | A |  | Radius (a) | 0.011547 | m
| Distance from cable (r ) | 1 | m |  | Distance from cable (r ) | 0.2 | m |  | Diameter of coil | 0.023094 | m
[9 empty] | Conductor length | 1000.6578 | m
| a0 | -0.13256 |  |  | gamma | 0.62832
| a1 | -3.5016 |  |  | F factor | 0.33301
| a2 | 0.1 |  |  | Bo | 2.8868e-05
| a3 | 1.9379 |  |  | B (untwisted) | 30.6186
| LnI | 5.9915 |  |  | B (twisted) | 10.1962
| LnG | -2.6827
| LnA | -3.5342
| LnB | -0.22539
| Magnetic field, B | 0.7982 | uT
| Method 1 |  |  | Method 1
| Line calculation - single circuit |  |  | Line calculation - double circuit
| Only applicable for typical cable sizes |  |  | Only applicable for typical cable sizes
| Height above ground | 0 |  | Distance between |  | 0.9
| Depth of cable | 1 |  | circuit centres
| Distance from centre | Distance from cable | Magnetic field (uT) | Circuit 1 | Circuit 2 | B1 | B2 | B - two circuits (worst case)
| 0 | 1 | 0.7982 | 1.0966 | 1.0966 | 0.55992 | 0.55992 | 1.1198
| 0.1 | 1.005 | 0.78363 | 1.1413 | 1.0595 | 0.47585 | 0.6413 | 1.1171
| 0.2 | 1.0198 | 0.74195 | 1.1927 | 1.0308 | 0.39494 | 0.71258 | 1.1075
| 0.3 | 1.044 | 0.6787 | 1.25 | 1.0112 | 0.32113 | 0.7659 | 1.087
| 0.4 | 1.077 | 0.60138 | 1.3124 | 1.0012 | 0.25656 | 0.79453 | 1.0511
| 0.5 | 1.118 | 0.51781 | 1.3793 | 1.0012 | 0.2019 | 0.79453 | 0.99643
| 0.6 | 1.1662 | 0.4347 | 1.45 | 1.0112 | 0.15685 | 0.7659 | 0.92276
| 0.7 | 1.2207 | 0.35697 | 1.524 | 1.0308 | 0.12052 | 0.71258 | 0.8331
| 0.8 | 1.2806 | 0.28762 | 1.6008 | 1.0595 | 0.09173 | 0.6413 | 0.73303
| 0.9 | 1.3454 | 0.22799 | 1.68 | 1.0966 | 0.069252 | 0.55992 | 0.62917
| 1 | 1.4142 | 0.17822 | 1.7614 | 1.1413 | 0.051918 | 0.47585 | 0.52776
| 1.1 | 1.4866 | 0.13767 | 1.8446 | 1.1927 | 0.038686 | 0.39494 | 0.43362
| 1.2 | 1.562 | 0.10526 | 1.9294 | 1.25 | 0.028675 | 0.32113 | 0.34981
| 1.3 | 1.6401 | 0.079778 | 2.0156 | 1.3124 | 0.021157 | 0.25656 | 0.27772
| 1.4 | 1.7205 | 0.060011 | 2.103 | 1.3793 | 0.015547 | 0.2019 | 0.21745
| 1.5 | 1.8028 | 0.044848 | 2.1915 | 1.45 | 0.011384 | 0.15685 | 0.16824
| 1.6 | 1.8868 | 0.033327 | 2.2809 | 1.524 | 0.0083095 | 0.12052 | 0.12883
| 1.7 | 1.9723 | 0.024644 | 2.3712 | 1.6008 | 0.0060484 | 0.09173 | 0.097778
| 1.8 | 2.0591 | 0.018145 | 2.4622 | 1.68 | 0.0043917 | 0.069252 | 0.073644
| 1.9 | 2.1471 | 0.013309 | 2.5539 | 1.7614 | 0.0031817 | 0.051918 | 0.055099
| 2 | 2.2361 | 0.0097296 | 2.6462 | 1.8446 | 0.0023005 | 0.038686 | 0.040987
a

## VA to Amp calcs
EGN 423: EMF Calculator
Version 4 - 10 March 2016
VA to Amps calculations |  |  |  |  | Multicore cables
VA to Amps
Vline = | 132000 | V
VA | 240000000 | VA = | 240 | MVA
Vph | 76210.2355 | V
Impedence | 72.6 | ohms
Amps | 1049.7278 | amps
Amps to VA
Vline = | 132000 | V
Amps | 1043 | amps
VA | 238461826.9829 | VA = | 238.4618 | MVA
Vph | 76210.2355 | V
Impedence | 73.0683 | ohms